## Self-Review Tool
RERC Advanced Wood Heating System Application Self-Review Tool
Use this tool to assess if your application will be accepted as is or if you will be asked clarifying questions. This is not meant as a design tool for boiler sizing.
| Please provide input in cells highlighted in yellow |  | If any issues are identified in the range of values, they will appear as red text in the lower box (step 3)
Step 1: | Input Data from Application Form:
| For all applications: | Pellet Boiler Output (Btu/hr)
Thermal Storage Capacity (gallons, leave blank if none)
|  | Backup fossil fuel system in place (yes/no) | yes | 120%
|  | Biomass boiler provides domestic hot water (yes/no) | yes | 120%
|  | Capacity of pellet storage (tons) | 2
|  | Sq Ft Heated space (sq ft) | 0 | 120%
|  | Calculated peak load (Btu/hr) | 0
Step 2: | Input Annual Heating Fuel Use Information |  |  | MMBtu/unit:
| If historical fuel usage was used to calculate peak boiler capacity, provide inputs for each fuel type used at the building: | If oil was used, 3 year average gallons of fuel consumed | 0 | 0.11056 | per gallon oil
|  | If propane was used, 3 year average gallons of fuel consumed |  | 0.07328 | per gallon propane
|  | If wood was used, 3 year average cords of wood burned |  | 13.2 | per cord seasoned wood
|  | If natural gas was used, 3 year average therms natural gas |  | 0.08 | per therm natural gas
Note: details on methodology used needs to be provided if prior fuel consumption was not used to calculate peak load for the building
Step 3: | Review Results |  |  | Expected range (unless justification provided): | Potential issues that may result in requests for additional documentation (no issues if the box below is blank):
| If any red text or flags appears to the right, you may be asked to provide additional details before the application is approved | Estimated annual heat load (MMBtu) | 0 |  | Provide details in your application on method used to estimate annual heat load
|  | Thermal storage capacity for boiler output (gallon thermal storage/ kBTU boiler capacity) | 0 | 0.75 to 5 gallon/kBtu
|  | Pellet fuel storage capacity (Days of storage at fuel output) | #DIV/0! | over 14 days | #DIV/0!
|  | Annual heat demand in kBtu/ Sq Ft | #DIV/0! | 10-60 kBtu/Sq Ft | #DIV/0!
|  | Boiler size in BTU/ Sq Ft | #DIV/0! | 10-40 Btu/h/sq ft | #DIV/0!
|  | Boiler size percent of peak load | #DIV/0! | <100% if backup fuel present and no hot water, <120% if hot water, <130% if sole heating source, <100% if enough thermal storage | #DIV/0!
Note:
If system has fully redundant fossil fueled boiler back-up, pellet boiler should be sized to cover between 50% and 90% of peak hourly demand - this should still cover 90-100% of annual load